# Report Template: Environmental Monitoring Data Trending

This is a ready-to-use periodic trend report template for environmental monitoring (EM) data. Replace every <<FILL: ...>> placeholder with your own specifics. A worked filled specimen follows the template. The purpose of this report is to turn plate counts into a signal: to catch slow drift, resident flora, and cross-method patterns before any single result breaches an action level, and to feed the contamination control strategy. A trend report that is generated, filed, and never acted on is worse than none, because it documents that the signal was seen and ignored.

# Document control header

| Field | Entry |
| --- | --- |
| Report title | Environmental Monitoring Data Trend Report |
| Report number | <<FILL: REP-ID, e.g. REP-QC-031-Q2-2026>> |
| Linked SOP | <<FILL: SOP-ID for EM program / trending>> |
| Reporting period | <<FILL: from date>> to <<FILL: to date>> |
| Frequency | Monthly / Quarterly / Annual |
| Scope (suites / grades) | <<FILL>> |
| Prepared by | <<FILL: role, e.g. EM program owner>> |

# 1. Purpose and scope

This report summarizes EM data for <<FILL: COMPANY NAME>> over the reporting period across the suites and grades in scope, to assess whether the aseptic environment is stable, to surface out-of-trend signals, to confirm or re-derive alert and action levels, and to feed the contamination control strategy (CCS) and the EM site map. It covers viable air, viable surface, personnel monitoring, and non-viable particulate.

# 2. Data set and completeness

State exactly what was analyzed so the report is re-derivable.

| Field | Entry |
| --- | --- |
| Data source | <<FILL: LIMS / system name and query/report ID>> |
| Sessions in period | <<FILL: count>> |
| Total samples analyzed | <<FILL: count, by method>> |
| Plate reconciliation gaps in period | <<FILL: count, with references>> (target: zero) |
| Excluded results (with justification) | <<FILL: count + reference>> |
| Data extract date and analyst | <<FILL>> |

A statement that the data set is complete and reconciled, with no unaccounted plates, is the foundation of the report. If reconciliation gaps exist, list them and their deviation references here.

# 3. Trending by grade and method

Report viable results as recovery rate (the fraction of samples showing any growth) for near-zero zones, and add summary statistics where the data supports them. For Grade A, recovery rate is the primary metric; a mean is meaningless when almost every plate reads zero.

| Grade | Method | Samples | Samples with recovery | Recovery rate | Alerts crossed | Actions crossed | Prior-period recovery rate |
| --- | --- | --- | --- | --- | --- | --- | --- |
| A | Viable air | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> |
| A | Settle | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> |
| A | Surface (contact) | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> |
| A | Personnel | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> |
| B | (each method) | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> |
| C | (each method) | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> |
| D | (each method) | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> |

For non-viable particulate, report whether continuous Grade A/B monitoring stayed within limits during operations and list any documented excursions and their references: <<FILL>>.

# 4. Site-level signals

Identify any site whose recovery rate is rising across periods, even where no single result crossed an action level. Rising recovery rate is the early signal of a degrading environment.

| Site ID | Location | Grade | This period | Prior period | Two periods ago | Trend read |
| --- | --- | --- | --- | --- | --- | --- |
| <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL>> | <<FILL: stable / rising / out-of-trend>> |

# 5. Resident-organism analysis

A recurring organism at a recurring location is a resident, a sign of a niche the cleaning program is not reaching, an ingress source, or a water source. This is more concerning than a one-off skin commensal.

| Site / area | Most frequent isolate | Recurrences in period | Source class | Resident? | Action |
| --- | --- | --- | --- | --- | --- |
| <<FILL>> | <<FILL>> | <<FILL>> | People / Ingress-materials / Water / Other | <<FILL>> | <<FILL: monitor / investigate / OOT raised>> |

Note any shift in the dominant flora (for example from transient skin organisms to a persistent mold), any seasonal or shift-correlated pattern, and any new isolate added to the house-flora library: <<FILL>>.

# 6. Cross-method and cross-program correlation

Patterns that no single data stream shows on its own:

Non-viable excursions coinciding with viable hits at the same location and time: <<FILL>>

Personnel monitoring failures clustering with active-air rises: <<FILL>>

EM signals aligning with media fill results or specific interventions: <<FILL>>

Correlation with utility (water/gas) monitoring or with maintenance/HVAC events: <<FILL>>

# 7. Out-of-trend (OOT) determinations and excursions in period

| Reference | Site | Signal | Determination | Deviation / CAPA |
| --- | --- | --- | --- | --- |
| <<FILL>> | <<FILL>> | <<FILL: rising recovery rate / resident organism / action breach>> | <<FILL: OOT confirmed / not OOT>> | <<FILL: DEV/CAPA number or N/A>> |

A doubling recovery rate with a shifting dominant isolate is an OOT signal that should open a proactive investigation before any action-level breach, which is exactly what this review exists to catch.

# 8. Alert and action level review

| Field | Entry |
| --- | --- |
| Levels reviewed this period (Yes/No) | <<FILL>> |
| Statistical basis re-derivable from this data set (Yes/No) | <<FILL>> |
| Any level proposed for change (with rationale) | <<FILL: none, or proposed change + data basis>> |
| Confirmation each action level is at or below the regulatory limit | <<FILL>> |
| Confirmation each alert sits below its action level | <<FILL>> |
| Next scheduled re-derivation | <<FILL: date>> |

# 9. Conclusions and CCS feedback

| Field | Entry |
| --- | --- |
| Overall environmental state | <<FILL: in control / drifting / out of control>> |
| Key signals this period | <<FILL>> |
| Site map changes recommended | <<FILL: add/remove/reprioritize sites with rationale>> |
| Actions and CAPAs opened or tracked | <<FILL>> |
| Feedback to the contamination control strategy | <<FILL>> |
| Cleaning / disinfectant program feedback | <<FILL: e.g. add sporicidal frequency where mold recurs>> |

# 10. Acceptance criteria for this report

The data set is stated, complete, reconciled, and re-derivable (source, query, extract date).

Viable data in near-zero zones is trended by recovery rate, not mean CFU.

Rising recovery rates are flagged even without an action-level breach.

Resident organisms are identified and distinguished from transients by source class.

Alert and action levels are confirmed at or below the regulatory limit, with alert below action.

Every OOT signal has a determination and, where confirmed, a deviation or CAPA reference.

The report is signed, dated, and its recommendations are routed to the CCS and the site map.

# 11. References

EU GMP Annex 1, Manufacture of Sterile Medicinal Products (trending, contamination control strategy, continuous Grade A/B monitoring).

FDA Guidance for Industry, Sterile Drug Products Produced by Aseptic Processing, Current Good Manufacturing Practice.

21 CFR 211.113 and 211.192.

USP <1116> Microbiological Control and Monitoring of Aseptic Processing Environments (contamination recovery rates, low-count statistics).

ICH Q9, Quality Risk Management.

Confirm the current version and clause numbers before issue.

# 12. Approvals

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| Prepared by (EM program owner) | <<FILL>> |  |  |
| Reviewed by (QC Micro Lead) | <<FILL>> |  |  |
| Approved by (QA) | <<FILL>> |  |  |

──────────────────────────────

# Filled specimen

The following shows the trend section completed for one Grade B surface site over four quarters, so you can see how an inspector expects a trend read to land. The numbers and organisms are illustrative; replace them with your own.

Section 5, resident-organism analysis, site B-12 (Grade B fill-line surface):

| Quarter | Samples | Samples with recovery | Recovery rate | Most frequent isolate |
| --- | --- | --- | --- | --- |
| Q1 | 90 | 1 | 1.1% | Staphylococcus (skin) |
| Q2 | 90 | 2 | 2.2% | Staphylococcus (skin) |
| Q3 | 90 | 5 | 5.6% | Aspergillus (mold) |
| Q4 | 90 | 8 | 8.9% | Aspergillus (mold) |

Trend read. No single result exceeded the Grade B action level. But the recovery rate roughly doubled each quarter, and the dominant isolate shifted from a transient skin organism to a persistent mold. A mold recurring at one location points to ingress or a wet, uncleanable niche, not a gowning slip. This is an out-of-trend signal recorded in section 7 (reference OOT-2026-0019), and it opened a proactive investigation (DEV-2026-0240, CAPA-2026-0112) before any action-level breach. A mean-CFU chart would have hidden this, the counts are tiny, but the recovery-rate trend is unmistakable.

Conclusion and CCS feedback (section 9, extract). Overall state: drifting at site B-12, in control elsewhere. Key signal: rising mold recovery at the fill-line surface. Site map change: added a contact site at the adjacent floor drain and the nearest door gasket. CCS feedback: door gasket integrity and drain hygiene added to the CCS review; sporicidal disinfectant frequency at the fill-line floor increased pending the investigation outcome.

What makes this report defensible is that it acted on a signal a single result never raised. The recovery rate, not the count, told the story, and the report routed it to a deviation, a CAPA, a site-map change, and the CCS rather than filing it.

# Common inspection findings this report prevents

Trend reports generated and filed but never acted on, documenting that the signal was seen and ignored.

Mean-CFU trending in clean zones, which hides a rising recovery rate because most plates read zero.

A static site map that ignores a hotspot the trend data revealed.

Resident organisms never distinguished from transients, so an ingress or water source is missed.

Alert and action levels never re-derived, drifting out of step with the room's actual behavior.

A trend signal with no out-of-trend determination and no link to a deviation or CAPA.

# How to adapt this report template

Set your report number, period, and frequency in the header, and link it to your EM/trending SOP.

Replace the grade-and-method table in section 3 with your actual suites, grades, and methods.

Use recovery rate as the primary viable metric in near-zero zones; add percentile statistics only where the distribution supports them.

Point section 9 feedback at your real CCS, site map, and cleaning/disinfectant procedures by document number.

Confirm every regulation in section 11 against the current published version before issue.